## Data
BELOW GRADE DATA |  | For the ground floor type use:
z2 | 1.8 | 1 | 200 mm block wall, brick facing
Wall Resistance | 0.259 | 2 | 100 mm block wall, brick facing
Width1 | 6 | 3 | Metal stud wall, stucco
Width2 | 8 | 4 | Poured concrete wall with duct near perimeter
T inside | 20
T mean ground | 5
T ground amplitude | 2
z1 | 0.1
Uninsulation resistance | 0.94
Ground floor type | 2
Is the groud floor insulated? (Y/N) | Y
Internal temperature of the building | 24

## Table
| N | Y
1 | 1.17 | 0.86
2 | 1.45 | 0.85
3 | 2.07 | 0.92
4 | 3.67 | 1.24

## Results
Below Walls Loss [W] | 817.6569 | U wall [w/m2.K] | 0.95431 | Area wall [m2] | 50.4
Below Floor Loss [W] | 166.6473 | U Floor [w/m2.K] | 0.20422 | Area Floor [m2] | 48
Roof Loss [W] | 95.2 | N/A | 0 | N/A | 0
Total Heat Loss [W] | 1079.5042 | N/A | 0 | N/A | 0