## Results-Situation 1
Results | Heating Load [W] | Cooling Load [W] | Location Characteristics
Opaque walls |  |  | Location | Stockholm
Roof/Ceiling | 8317.7172 | 2536.3003 | Latitude | 60
Exterior Walls | 2428.7914 | 802.5666 | Winter Outlet Temperature[°C] | -5
Doors | 161.0169 | 52.5331 | Summer Outlet Temperature[°C] | 27
Floor | 2707.3864 | -165.692 | Summer specific humidity [kgv/kg_D.A.] | 0.103
Total Opaque | 13614.9119 | 3225.708 | Summer Daily Range [°C] | 9
Fenestration |  |  | Summer enthalpy value [kJ/kg_D.A.] | 52
Total Fenestration | 1302.6375 | 2643.9129 | Set Data
Below Grade |  |  | Winter Ambient Temperature [°C] | 20
Below Walls |  |  | Summer Ambient Temperature [°C] | 24
Below Floor |  |  | Summer Ambient specific humidity [kgv/kg_D.A.] | 0.0093
Total Below Grade |  |  | Summer Ambient enthalpy value [kJ/kg_D.A.] | 47.8
Vent./Inf.
V/I sensible | 15455.7907 | 1305.6247
V/I latent |  | 5336.7316
Internal Gains
Internal Sensible |  | 576
Internal Latent |  | 113
Subtotal sensible
Subtotal sensible | 30373.3401 | 7751.2457
Duct losses
Duct losses | 4859.7344 | 2557.9111
Total
Total load sensible | 35233.0745 | 10309.1567
Total load latent |  | 5449.7316

## Results-Situation 2
Results | Heating Load [W] | Cooling Load [W] | Location Characteristics
Opaque walls |  |  | Location | Munich
Roof/Ceiling | 7319.5911 | 3000.9908 | Latitude | 50
Exterior Walls | 2137.3364 | 940.0122 | Winter Outlet Temperature[°C] | -2
Doors | 141.6949 | 61.5298 | Summer Outlet Temperature[°C] | 29
Floor | 2382.5 | -63.8943 | Summer specific humidity [kgv/kg_D.A.] | 0.11
Total Opaque | 11981.1225 | 3938.6385 | Summer Daily Range [°C] | 8
Fenestration |  |  | Summer enthalpy value [kJ/kg_D.A.] | 54
Total Fenestration | 1146.321 | 2594.7346 | Set Data
Below Grade |  |  | Winter Ambient Temperature [°C] | 20
Below Walls |  |  | Summer Ambient Temperature [°C] | 24
Below Floor |  |  | Summer Ambient specific humidity [kgv/kg_D.A.] | 0.0093
Total Below Grade |  |  | Summer Ambient enthalpy value [kJ/kg_D.A.] | 47.8
Vent./Inf.
V/I sensible | 13366.3462 | 2214.658
V/I latent |  | 5837.2031
Internal Gains
Internal Sensible |  | 576
Internal Latent |  | 113
Subtotal sensible
Subtotal sensible | 26493.7897 | 9324.0311
Duct losses
Duct losses | 4239.0064 | 3076.9303
Total
Total load sensible | 30732.796 | 12400.9614
Total load latent |  | 5950.2031

## Results-Situation 3
Results | Heating Load [W] | Cooling Load [W] | Location Characteristics
Opaque walls |  |  | Location | Naples
Roof/Ceiling | 6654.1738 | 3481.9293 | Latitude | 45
Exterior Walls | 1943.0331 | 1082.2635 | Winter Outlet Temperature[°C] | 0
Doors | 128.8136 | 70.8411 | Summer Outlet Temperature[°C] | 32
Floor | 2165.9091 | -17.3273 | Summer specific humidity [kgv/kg_D.A.] | 0.123
Total Opaque | 10891.9295 | 4617.7066 | Summer Daily Range [°C] | 10
Fenestration |  |  | Summer enthalpy value [kJ/kg_D.A.] | 56
Total Fenestration | 1042.11 | 2719.8654 | Set Data
Below Grade |  |  | Winter Ambient Temperature [°C] | 20
Below Walls |  |  | Summer Ambient Temperature [°C] | 24
Below Floor |  |  | Summer Ambient specific humidity [kgv/kg_D.A.] | 0.0093
Total Below Grade |  |  | Summer Ambient enthalpy value [kJ/kg_D.A.] | 47.8
Vent./Inf.
V/I sensible | 12008.9514 | 3636.1332
V/I latent |  | 6763.1485
Internal Gains
Internal Sensible |  | 576
Internal Latent |  | 113
Subtotal sensible
Subtotal sensible | 23942.9909 | 11549.7053
Duct losses
Duct losses | 3830.8785 | 3811.4027
Total
Total load sensible | 27773.8694 | 15361.108
Total load latent |  | 6876.1485

## Results-Situation 4
Results | Heating Load [W] | Cooling Load [W] | Location Characteristics
Opaque walls |  |  | Location | Heraklion
Roof/Ceiling | 5988.7564 | 4024.6098 | Latitude | 40
Exterior Walls | 1748.7298 | 1242.7768 | Winter Outlet Temperature[°C] | 2
Doors | 115.9322 | 81.3477 | Summer Outlet Temperature[°C] | 35
Floor | 1949.3182 | 59.5625 | Summer specific humidity [kgv/kg_D.A.] | 0.13
Total Opaque | 9802.7366 | 5408.2968 | Summer Daily Range [°C] | 11
Fenestration |  |  | Summer enthalpy value [kJ/kg_D.A.] | 60
Total Fenestration | 937.899 | 2743.5636 | Set Data
Below Grade |  |  | Winter Ambient Temperature [°C] | 20
Below Walls |  |  | Summer Ambient Temperature [°C] | 24
Below Floor |  |  | Summer Ambient specific humidity [kgv/kg_D.A.] | 0.0093
Total Below Grade |  |  | Summer Ambient enthalpy value [kJ/kg_D.A.] | 47.8
Vent./Inf.
V/I sensible | 10680.011 | 5127.1187
V/I latent |  | 7362.5221
Internal Gains
Internal Sensible |  | 576
Internal Latent |  | 113
Subtotal sensible
Subtotal sensible | 21420.6466 | 13854.9791
Duct losses
Duct losses | 3427.3034 | 4572.1431
Total
Total load sensible | 24847.95 | 18427.1222
Total load latent |  | 7475.5221

## Results-Situation 5
Results | Heating Load [W] | Cooling Load [W] | Location Characteristics
Opaque walls |  |  | Location | Cairo
Roof/Ceiling | 4990.6303 | 5278.9493 | Latitude | 30
Exterior Walls | 1457.2748 | 1613.7837 | Winter Outlet Temperature[°C] | 5
Doors | 96.6102 | 105.6325 | Summer Outlet Temperature[°C] | 40
Floor | 1624.4318 | 359.5409 | Summer specific humidity [kgv/kg_D.A.] | 0.15
Total Opaque | 8168.9471 | 7357.9063 | Summer Daily Range [°C] | 7
Fenestration |  |  | Summer enthalpy value [kJ/kg_D.A.] | 64
Total Fenestration | 781.5825 | 3092.761 | Set Data
Below Grade |  |  | Winter Ambient Temperature [°C] | 20
Below Walls |  |  | Summer Ambient Temperature [°C] | 24
Below Floor |  |  | Summer Ambient specific humidity [kgv/kg_D.A.] | 0.0093
Total Below Grade |  |  | Summer Ambient enthalpy value [kJ/kg_D.A.] | 47.8
Vent./Inf.
V/I sensible | 8739.9526 | 7766.5617
V/I latent |  | 8938.0251
Internal Gains
Internal Sensible |  | 576
Internal Latent |  | 113
Subtotal sensible
Subtotal sensible | 17690.4823 | 18793.229
Duct losses
Duct losses | 2830.4772 | 6201.7656
Total
Total load sensible | 20520.9594 | 24994.9946
Total load latent |  | 9051.0251