## WindowData
Name | Direction | Height | Width | Frame_type | Frame_Material | ID | Attachment | Overhang_length | Overhang_height | Int_shade_type | Int_shade_material | Int_shade_close
W1 | W | 0.9 | 0.9 | Fixed | W | 5a | None | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
W2 | W | 0.9 | 0.9 | Operable | W | 5a | Insect_screen | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
W3 | W | 1.8 | 1.2 | Fixed | W | 5a | None | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
W4 | W | 1.8 | 1.2 | Operable | W | 5a | Insect_screen | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
W5 | W | 2.4 | 1.8 | Fixed | W | 5a | None | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
S1 | S | 1.2 | 1.2 | Fixed | W | 5a | None | 0 | 0 | Drapes | Closed_weave_medium | 0.5
S2 | S | 1.2 | 1.2 | Operable | W | 5a | Insect_screen | 0 | 0 | Drapes | Closed_weave_medium | 0.5
E1 | E | 0.9 | 0.9 | Fixed | W | 5a | None | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
E2 | E | 0.9 | 0.9 | Operable | W | 5a | Insect_screen | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
E3 | E | 1.2 | 1.2 | Fixed | W | 5a | None | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
E4 | E | 1.2 | 1.2 | Operable | W | 5a | Insect_screen | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
E5 | E | 1.2 | 1.2 | Fixed | W | 5a | None | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
E6 | E | 1.2 | 1.2 | Operable | W | 5a | Insect_screen | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
E7 | E | 1.2 | 1.2 | Fixed | W | 5a | None | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5
E8 | E | 1.2 | 1.2 | Operable | W | 5a | Insect_screen | 0.6 | 0 | Drapes | Closed_weave_medium | 0.5

## Results
2 | Area | U | HF | Tx | F_Shd | PXI | SHGC | IAC | FFS | CF
W1 | 0.81 | 2.84 | 56.8 | 1 | 0.72685 | 716.719 | 0.67 | 0.69472 | 0.56 | 191.4495
W2 | 0.81 | 2.87 | 57.4 | 0.64 | 0.72685 | 516.4846 | 0.57 | 0.69472 | 0.56 | 119.2116
W3 | 2.16 | 2.84 | 56.8 | 1 | 0.36342 | 930.2771 | 0.67 | 0.84736 | 0.56 | 300.3924
W4 | 2.16 | 2.87 | 57.4 | 0.64 | 0.36342 | 730.0427 | 0.57 | 0.84736 | 0.56 | 202.1386
W5 | 4.32 | 2.84 | 56.8 | 1 | 0.27257 | 983.6666 | 0.67 | 0.88552 | 0.56 | 331.4502
S1 | 1.44 | 2.84 | 56.8 | 1 | 0 | 190.945 | 0.67 | 1 | 0.47 | 64.7578
S2 | 1.44 | 2.87 | 57.4 | 0.64 | 0 | 122.2048 | 0.57 | 1 | 0.47 | 37.4168
E1 | 0.81 | 2.84 | 56.8 | 1 | 0.72685 | 590.033 | 0.67 | 0.69472 | 0.31 | 89.7676
E2 | 0.81 | 2.87 | 57.4 | 0.64 | 0.72685 | 435.4056 | 0.57 | 0.69472 | 0.31 | 58.1275
E3 | 1.44 | 2.84 | 56.8 | 1 | 0.54514 | 696.8121 | 0.67 | 0.77104 | 0.31 | 116.2206
E4 | 1.44 | 2.87 | 57.4 | 0.64 | 0.54514 | 542.1846 | 0.57 | 0.77104 | 0.31 | 78.5471
E5 | 1.44 | 2.84 | 56.8 | 1 | 0.54514 | 696.8121 | 0.67 | 0.77104 | 0.31 | 116.2206
E6 | 1.44 | 2.87 | 57.4 | 0.64 | 0.54514 | 542.1846 | 0.57 | 0.77104 | 0.31 | 78.5471
E7 | 1.44 | 2.84 | 56.8 | 1 | 0.54514 | 696.8121 | 0.67 | 0.77104 | 0.31 | 116.2206
E8 | 1.44 | 2.87 | 57.4 | 0.64 | 0.54514 | 542.1846 | 0.57 | 0.77104 | 0.31 | 78.5471

## U_Operable_Fenestration
Type | Glazing | ID | Aluminum | Aluminum with Thermal Break | Reinforced Aluminum Clad Wood | Wood/Vinyl | Insulated Fiberglass/Vinyl
Type | Glazing | ID | A | AT | RA | W | IF
Clear | 1 | 1a | 7.24 | 6.12 | 5.14 | 5.05 | 4.61
| 2 | 5a | 4.62 | 3.42 | 3.00 | 2.87 | 5.83
| 3 | 29a | 3.80 | 2.60 | 2.25 | 2.19 | 1.91
Low-e,low-solar | 2 | 25a | 3.83 | 2.68 | 2.33 | 2.21 | 1.89
| 3 | 40c | 3.22 | 2.07 | 1.76 | 1.71 | 1.45
Low-e,high-solar | 2 | 17c | 4.05 | 2.89 | 2.52 | 2.39 | 2.07
| 3 | 32c | 3.54 | 2.36 | 2.02 | 1.97 | 1.70
Heat-absorbing | 1 | 1c | 7.24 | 6.12 | 5.14 | 5.05 | 4.61
| 2 | 5c | 4.62 | 3.42 | 3.00 | 2.87 | 2.53
| 3 | 29c | 3.80 | 2.60 | 2.25 | 2.19 | 1.91
Reflective | 1 | 1l | 7.24 | 6.12 | 5.14 | 5.05 | 4.61
| 2 | 5p | 4.62 | 3.42 | 3.00 | 2.87 | 2.53
| 3 | 29c | 3.80 | 2.60 | 2.25 | 2.19 | 1.91

## U_Fixed_Fenestration
Type | Glazing | ID | Aluminum | Aluminum with Thermal Break | Reinforced Aluminum Clad Wood | Wood/Vinyl | Insulated Fiberglass/Vinyl
Type | Glazing | ID | A | AT | RA | W | IF
Clear | 1 | 1a | 6.42 | 6.07 | 5.55 | 5.55 | 5.35
| 2 | 5a | 3.61 | 3.22 | 2.86 | 2.84 | 2.72
| 3 | 29a | 2.76 | 2.39 | 2.05 | 2.01 | 1.93
Low-e,low-solar | 2 | 25a | 2.75 | 2.36 | 2.03 | 2.01 | 1.90
| 3 | 40c | 2.13 | 1.76 | 1.44 | 1.40 | 1.33
Low-e,high-solar | 2 | 17c | 2.99 | 2.60 | 2.26 | 2.24 | 2.13
| 3 | 32c | 2.47 | 2.10 | 1.77 | 1.73 | 1.66
Heat-absorbing | 1 | 1c | 6.42 | 6.07 | 5.55 | 5.55 | 5.35
| 2 | 5c | 3.61 | 3.22 | 2.86 | 2.84 | 2.72
| 3 | 29c | 2.76 | 2.39 | 2.05 | 2.01 | 1.93
Reflective | 1 | 1l | 6.42 | 6.07 | 5.55 | 5.55 | 5.35
| 2 | 5p | 3.61 | 3.22 | 2.86 | 2.84 | 2.72
| 3 | 29c | 2.76 | 2.39 | 2.05 | 2.01 | 1.93

## SHGC_Operable_Fenestration
|  |  | Aluminum | Aluminum with Thermal Break | Reinforced Aluminum Clad Wood | Wood/Vinyl | Insulated Fiberglass/Vinyl
|  |  | A | AT | RA | W | IF
Clear | 1 | 1a | 0.75 | 0.75 | 0.64 | 0.64 | 0.64
| 2 | 5a | 0.67 | 0.67 | 0.57 | 0.57 | 0.57
| 3 | 29a | 0.60 | 0.60 | 0.51 | 0.51 | 0.51
Low-e,low-solar | 2 | 25a | 0.37 | 0.37 | 0.31 | 0.31 | 0.31
| 3 | 40c | 0.25 | 0.25 | 0.21 | 0.21 | 0.21
Low-e,high-solar | 2 | 17c | 0.62 | 0.62 | 0.52 | 0.52 | 0.52
| 3 | 32c | 0.55 | 0.55 | 0.46 | 0.46 | 0.46
Heat-absorbing | 1 | 1c | 0.64 | 0.64 | 0.54 | 0.54 | 0.54
| 2 | 5c | 0.55 | 0.55 | 0.46 | 0.46 | 0.46
| 3 | 29c | 0.31 | 0.31 | 0.26 | 0.26 | 0.26
Reflective | 1 | 1l | 0.28 | 0.28 | 0.24 | 0.24 | 0.24
| 2 | 5p | 0.27 | 0.27 | 0.22 | 0.22 | 0.22
| 3 | 29c | 0.31 | 0.31 | 0.26 | 0.26 | 0.26

## SHGC_Fixed_Fenestration
|  |  | Aluminum | Aluminum with Thermal Break | ReinforcedAluminum Clad Wood | Wood/Vinyl | Insulated Fiberglass/Vinyl
|  |  | A | AT | RA | W | IF
Clear | 1 | 1a | 0.78 | 0.78 | 0.75 | 0.75 | 0.75
| 2 | 5a | 0.69 | 0.69 | 0.67 | 0.67 | 0.67
| 3 | 29a | 0.62 | 0.62 | 0.60 | 0.60 | 0.60
Low-e,low-solar | 2 | 25a | 0.38 | 0.38 | 0.36 | 0.36 | 0.36
| 3 | 40c | 0.25 | 0.25 | 0.24 | 0.24 | 0.24
Low-e,high-solar | 2 | 17c | 0.64 |  | 0.61 | 0.61 | 0.61
| 3 | 32c | 0.56 | 0.56 | 0.54 | 0.54 | 0.54
Heat-absorbing | 1 | 1c | 0.66 | 0.66 | 0.64 | 0.64 | 0.64
| 2 | 5c | 0.56 | 0.56 | 0.54 | 0.54 | 0.54
| 3 | 29c | 0.31 | 0.31 | 0.30 | 0.30 | 0.30
Reflective | 1 | 1l | 0.29 | 0.29 | 0.27 | 0.27 | 0.27
| 2 | 5p | 0.27 | 0.27 | 0.26 | 0.26 | 0.26
| 3 | 29c | 0.31 | 0.31 | 0.30 | 0.30 | 0.30

## Peak_Irradiance
Table | 10 | Peak | Irradiance, | W/m2
Exposure
Latitude [°]
|  | 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
N | ED | 125 | 106 | 92 | 84 | 81 | 85 | 96 | 112 | 136
| Ed | 128 | 115 | 103 | 93 | 84 | 76 | 69 | 62 | 55
| Et | 253 | 221 | 195 | 177 | 166 | 162 | 164 | 174 | 191
NE | ED | 460 | 449 | 437 | 425 | 412 | 399 | 386 | 374 | 361
| Ed | 177 | 169 | 162 | 156 | 151 | 147 | 143 | 140 | 137
| Et | 637 | 618 | 599 | 581 | 563 | 546 | 529 | 513 | 498
NW | ED | 460 | 449 | 437 | 425 | 412 | 399 | 386 | 374 | 361
| Ed | 177 | 169 | 162 | 156 | 151 | 147 | 143 | 140 | 137
| Et | 637 | 618 | 599 | 581 | 563 | 546 | 529 | 513 | 498
E | ED | 530 | 543 | 552 | 558 | 560 | 559 | 555 | 547 | 537
| Ed | 200 | 196 | 193 | 190 | 189 | 188 | 187 | 187 | 187
| Et | 730 | 739 | 745 | 748 | 749 | 747 | 742 | 734 | 724
W | ED | 530 | 543 | 552 | 558 | 560 | 559 | 555 | 547 | 537
| Ed | 200 | 196 | 193 | 190 | 189 | 188 | 187 | 187 | 187
| Et | 730 | 739 | 745 | 748 | 749 | 747 | 742 | 734 | 724
SE | ED | 282 | 328 | 369 | 405 | 436 | 463 | 485 | 503 | 517
| Ed | 204 | 203 | 203 | 204 | 205 | 207 | 210 | 212 | 215
| Et | 485 | 531 | 572 | 609 | 641 | 670 | 695 | 715 | 732
SW | ED | 282 | 328 | 369 | 405 | 436 | 463 | 485 | 503 | 517
| Ed | 204 | 203 | 203 | 204 | 205 | 207 | 210 | 212 | 215
| Et | 485 | 531 | 572 | 609 | 641 | 670 | 695 | 715 | 732
S | ED | 0 | 60 | 139 | 214 | 283 | 348 | 408 | 464 | 515
| Ed | 166 | 193 | 196 | 200 | 204 | 209 | 214 | 219 | 225
| Et | 166 | 253 | 335 | 414 | 487 | 557 | 622 | 683 | 740
H | ED | 845 | 840 | 827 | 806 | 776 | 738 | 691 | 637 | 574
| Ed | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170 | 170
| Et | 1015 | 1010 | 997 | 976 | 946 | 908 | 861 | 807 | 744

## Shade_Line_Factor
Table | 12 | Shade | Line | Factors | (SLFs)
Exposure
Latitude [°]
| 20 | 25 | 30 | 35 | 40 | 45 | 50 | 55 | 60
N | 2.8 | 2.1 | 1.4 | 1.5 | 1.7 | 1.0 | 0.8 | 0.9 | 0.8
NE | 1.4 | 1.5 | 1.6 | 1.2 | 1.3 | 1.3 | 0.9 | 0.9 | 0.8
NW | 1.4 | 1.5 | 1.6 | 1.2 | 1.3 | 1.3 | 0.9 | 0.9 | 0.8
E | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.0 | 1.0 | 0.9 | 0.8
W | 1.2 | 1.2 | 1.1 | 1.1 | 1.1 | 1.0 | 1.0 | 0.9 | 0.8
SE | 2.1 | 1.8 | 2.0 | 1.7 | 1.5 | 1.6 | 1.4 | 1.2 | 1.1
SW | 2.1 | 1.8 | 2.0 | 1.7 | 1.5 | 1.6 | 1.4 | 1.2 | 1.1
S | 20.0 | 14.0 | 6.9 | 4.7 | 3.3 | 2.7 | 2.1 | 1.7 | 1.4

## Solar_Load_Factor
Table | 13 | Fenestration | Solar | Load | Factors | FFs
Exposure | Single Family Detached | Multifamily
N | 0.44 | 0.27
NE | 0.21 | 0.43
E | 0.31 | 0.56
SE | 0.37 | 0.54
S | 0.47 | 0.53
SW | 0.58 | 0.61
W | 0.56 | 0.65
NW | 0.46 | 0.57
H | 0.58 | 0.73

## Interior_Attenuation_Coefficien
Table | 14 | Interior | Attenuation | Coefficients | (IACcl)
Glazing Layers | Glazing Type | ID
|  |  | Drapes |  |  | Roller |  |  | Shades
|  |  | Open-Weave | Closed-Weave |  | Opaque |  | Translucent | Blinds
|  |  | Light | Dark | Light | Dark | White | Light | Medium | White
1 | Clear | 1a | 0.64 | 0.71 | 0.45 | 0.64 | 0.34 | 0.44 | 0.74 | 0.66
| Heat absorbing | 1c | 0.68 | 0.72 | 0.50 | 0.67 | 0.40 | 0.49 | 0.76 | 0.69
2 | Clear | 5a | 0.72 | 0.81 | 0.57 | 0.76 | 0.48 | 0.55 | 0.82 | 0.74
| Low-e high-solar | 17c | 0.76 | 0.86 | 0.64 | 0.82 | 0.57 | 0.62 | 0.86 | 0.79
| Low-e low-solar | 25a | 0.79 | 0.88 | 0.68 | 0.85 | 0.60 | 0.66 | 0.88 | 0.82
| Heat absorbing | 5c | 0.73 | 0.82 | 0.59 | 0.77 | 0.51 | 0.58 | 0.83 | 0.76